CONSUMER NOTICE OF LEAD AND COPPER RESULTS IN DRINKING WATER

Sisters of the Holy Cross Inc./ St. Mary’s College (Public Water Supply ID IN 5271025)

St. Joseph County Indiana

Date sampled: 08/13/2014

As part of our Indiana-approved drinking water monitoring program here at St. Mary’s, we recently sampled at ten different locations throughout campus, and tested those samples for lead and copper. The samples were selected based on plumbing considerations and campus accessibility. This report serves as notification to you of the results at each sampling site, as well as a consumer notification of the dangers of lead in drinking water.

The actual levels of lead and copper at each location are in the table below, along with the respective EPA Action Levels and Maximum Contaminant Level Goals (see Table Key)

| LOCATION | CONTAMINANT | RESULT mg/l | ACTION LEVEL mg/l | MCLG mg/l |
| --- | --- | --- | --- | --- |
| Central Utilities Lab | Copper | 0.009 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| Powerhouse Break Room | Copper | 0.015 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| Grounds Kitchenette | Copper | 0.006 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| McCandless Hall Kitchenette | Copper | 0.14 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| SPES Unica Women’s Restroom | Copper | 0.085 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| Madeleva Hall Faculty Lounge | Copper | 0.22 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| LeMans Hall Kitchenette | Copper | 0.065 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| College Dining Hall | Copper | 0.22 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| Convent Kitchenette | Copper | 0.069 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |
| Rosary Dining Hall Kitchen | Copper | 0.13 | 1.3 | 1.3 |
|  | Lead | < 0.0010 | 0.015 | 0 |

Table Key:

Action level (AL): The concentration of a contaminant if, which exceeded, triggers treatment or other requirements that a water system must follow to take corrective action

Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below which there is no known or expected risk to health. MCLG allows for a margin of safety

mg/l = milligrams per liter, or parts per million (ppm)

< indicates “less than”, meaning the contaminant was not detected at the lab procedural limits

These results indicate that lead was not detected in any of the samples. The copper levels were well below the respective Action Levels at each sampling location. If any results had exceeded the Action Level, our drinking water monitoring program provides for immediate remedial action, including prompt notification and/or closing of affected areas.

While very high levels of copper can be toxic, it is lead that is the primary concern in drinking water, because very low levels can cause significant harm, especially over long periods of time. Although lead was not detected in any of the samples, the following page explains the dangers of lead, and how to reduce your exposure to it in drinking water at home.

For more information about this report, contact Chris Cullison, Division Director of Facilities at (574) 284-5778, or e-mail ccullison@cscsisters.org.

## LEAD IN DRINKING WATER – WHAT IT MEANS AND HOW TO REDUCE EXPOSURE

Although the primary source of lead exposure for most children are deteriorating lead-based paint, lead-contaminated dust, and lead-contaminated soil, the USEPA estimates that 10% to 20% of human exposure to lead may come from drinking water.

Lead can cause serious health problems if too much enters your body from drinking water or other sources. Lead can cause damage to the brain and kidneys, and it can interfere with the production of red blood cells that carry oxygen to all parts of your body. The greatest risk of lead exposure is to infants, young children, and pregnant women. Scientists have linked the effects of lead on the brain with lowered IQ in children. Adults with kidney problems and high blood pressure can be affected by low levels of lead more than healthy adults. Lead is stored in the bones, and can be released later in life. During pregnancy, the child receives lead from the mother’s bones, which may affect brain development.

To reduce exposure to lead in drinking water (if applicable):

- Run your water to flush out lead. Run the water until it becomes cold.

- Use cold water for cooking and preparing baby formula. Do not cook with or drink water from the hot water tap; lead dissolves more easily in hot water.

- Do not boil water to remove lead. Boiling water will not reduce lead levels.

- Look for alternative sources for treatment of water. If your lead result is above 15 ppb, you may want to consider purchasing bottled water or a water filter. Read the package to be sure the filter is approved to reduce lead or contact NSF International at 800-NSF-8010 or visit www.nsf.org for information on performance standards for water filters.

- Identify if your plumbing fixtures contain lead. New faucets, fittings, and valves may contain up to 8% lead, including those advertised as “lead-free”, and may contribute lead to drinking water. You should be aware of this when choosing fixtures, and take precautions.

For more information on reducing lead exposure around the home and the health effects of lead, visit the U. S. EPA’s Website at www.epa.gov/lead, call the National Lead Information Center at 800-424-LEAD, or contact your health provider.